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	AUDIENCE
	· Electrical Contractors
· Field Work Force Officers


This Information Brief contains important information that affects the processes our people use.

Payphone Light Switch 042/00853

	Purpose
	To inform field work force and contractors that a non-standard, 2 pole switch that has been supplied through the Telstra stores system as a replacement part (042/00853) in the 42/400 FLPC & Telebox light, should not be used. 

	Background
	The HPM brand switch originally used in the 042/00400 FLPC & Telebox light was banned a number of years ago. However, despite this, the switch has been recently detected in Telstra stock. 
The switch may be hazardous in the light because the rocker may be dislodged after installation, exposing hazardous voltages on the switch contacts.

Persons working on the light fitting should be aware of these dangers.



	Requirements
	The incorrect HPM switch can be detected by its blue case. If this product has been installed in a light its casing can be easily seen through the gap between the rocker and the switch aperture.

When faulty switches are detected, they are to be reported to the local service operations manager/supervisor for replacement by an Electrician.

The correct switch is the Clipsal Cat No – 30MD-WE D/Pole White (42/853). Telstra’s stock holdings are being checked for correctness.

NOTE: The light switch only turns off the light, it does not isolate the power supply to the 240V/21V transformer located within the light assembly.

	Impact on HS&E requirements
	Direct exposure to hazardous voltages could result in electric shock. 

	Contact for further information
	Patrick Griffin

Telstra Payphone Services

Technical support

Ph: 02 9329 0651
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